## MISC-Cover Page
[8 empty] | OWNER Document No: |  | KLD-NVOE-MSE-TDS-3050SW-30001- |  |  | REV | A0
[8 empty] | COMPANY Document No: |  | KCD-FPU-EXE-NVOE-99-MRN-TDS-0007 |  |  | REV | A
SEA WATER COOLING PUMP & CENTRAL FW COOLING PUMP IMPELLER TECHNICAL DATASHEET | [11 empty] | Page No: 1 of 6
| PROJECT TITLE |  |  | : | PROVISION OF LEASE, OPERATE AND MAINTAIN (O&M) OF FLOATING PRODUCTION UNIT (FPU) FOR KELIDANG CLUSTER DEVELOPMENT PROJECT
| COMPANY |  |  | : | PETRONAS CARIGALI BRUNEI LTD
| CONTRACT NO |  |  | : | PCBL/2023/PROJECT/003
| DOCUMENT TITLE |  |  | : | SEA WATER COOLING PUMP & CENTRAL FW COOLING PUMP IMPELLER TECHNICAL DATASHEET
| DOCUMENT REVIEW CLASSIFICATION |  |  | : | X
| SECURITY CLASSIFICATION |  |  | : | OPEN
| SUBCONTRACTOR DOC NO |  |  | : | XXX-XXX-XXXXXX-XXXX
B0 |  | 08.05.2026 | Inter-Disciplinary Check |  |  | HSN | HHK |  | HHK
REV |  | DATE | DESCRIPTION |  |  | PREPARED | REVIEW |  | APPROVED | REVIEWED | VERIFIED |  | ACKN'D
[6 empty] | CONTRACTOR |  |  |  | COMPANY

## Revision History
|  |  |  | OWNER Document No: | KLD-NVOE-MSE-TDS-3050SW-30001- |  | REV
|  |  |  | COMPANY Document No: | KCD-FPU-EXE-NVOE-99-MRN-TDS-0007 |  | REV | A
SEA WATER COOLING PUMP & CENTRAL FW COOLING PUMP IMPELLER TECHNICAL DATASHEET | [5 empty] | Page No: 2 of 6
RECORD OF CHANGES
REVISION | DATE |  | DESCRIPTION
A0 | 2026-05-08 |  | Issued for Inter-DIsciplinary Check
HOLD LISTS
REVISION |  | DESCRIPTION
Note on A1: [스레드 댓글] 사용 중인 버전의 Excel에서 이 스레드 댓글을 읽을 수 있지만 파일을 이후 버전의 Excel에서 열면 편집 내용이 모두 제거됩니다. 자세한 정보: https://go.microsoft.com/fwlink/?linkid=870924. 댓글: Area Specific. Responsible engineer to change is Area Code 10 (FPU) / 20 (Topside) / 30 (Hull & Marine) / 40 (Mooring) / 50 (Subsea). To be deleted which not applicable

## Notes and holds
FPU KELIDANG
SEA WATER & CFW COOLING PUMP IMPELLER
TECHNICAL DATASHEET
| Document No: |  | KLD-NVOE-MSE-TDS-3050SW-30001 |  | Area | HULL & MARINE | Date: | 2026-05-08
| Tag No.: |  | SW-308X01/02 ¦ CW-308X01/02/03 |  | No. Req. | 1 | Prepared : | HSN
| Operation: |  | SEAWATER COOLING / CENTRAL FW COOLING |  | Project | FPU KELIDANG | Reviewed: | HHK
| Services: |  | PUMP IMPELLER RENEWAL |  | Job No. | N/A | Approved: | HHK
| Revision: |  | A0 |  | Serial No. | N/A | Page: | 3 | of | 6 | REV
SEA WATER & CFW COOLING PUMP IMPELLER
NOTES AND HOLDS
1 |  | STA = Supplier to advise ¦ STC = Supplier to confirm
2 |  | Supplier shall complete all items and return with technical bid.
3 |  | FPU design life: 15 years. No scheduled drydocking (UWILD notation).
4 |  | S.W. Pump impellers: AISI 316L SS Cast — grade shall be explicitly confirmed (OEM grade was unspecified).
5 |  | CFW Pump impellers: Cast Bronze ASTM B62 — original OEM material retained. Suitable for 55 °C FW service over 15-year design life.
6 |  | All impellers to be interchangeable with existing Naniwa FEV-250-2 pump casings. Dimensional drawings required with bid.
7 |  | Dynamic balancing: ISO 1940-1 Grade G2.5 minimum for all impellers. Balance certificates mandatory.
8 |  | ABS CLASS approval required for all items. Original classification: Lloyd's Register (LR).
9 |  | EN 10204 Type 3.1 material certificates required for all impellers and pressure-wetted parts.
10 |  | Dye penetrant (DP) test on all cast surfaces. ABS witnessed. Test report required.
11 |  | S.W. Pump mech. seal: SiC vs SiC faces, EPDM/FKM elastomers, rated ≥ 0.6 MPa, ≤ 60 °C.
12 |  | CFW Pump mech. seal: Carbon vs Ceramic faces, EPDM elastomers, rated ≥ 0.8 MPa, ≤ 70 °C.
13 |  | Export-grade packaging with corrosion inhibitor. Suitable for sea freight.
14 |  | Warranty: minimum 24 months from date of installation.
15 |  | 2-year operational spare parts list to be submitted with bid.

## Engine-1
FPU KELIDANG
SEA WATER & CFW COOLING PUMP IMPELLER
TECHNICAL DATASHEET
| Document No: |  |  |  | Area | Date:
| Tag No.: |  |  |  | No. Req. | By:
| Operation: |  |  |  | Project | Reviewed:
| Services: |  |  |  | Job No. | Approved:
| Revision: |  |  |  | Serial No. | Page: | 4 | of | 6 | REV
SEA WATER COOLING PUMP — IMPELLER
PUMP SERVICE DATA (REFER NOTES)
PUMP SERVICE DATA (REFER NOTES)
1 | Service |  | : | Main Seawater Cooling — FPU Machinery
2 | Tag No. |  | : | SW-308X01 / SW-308X02
3 | Impeller Sets |  | : | 2 sets (1 per pump: Duty + Standby)
4 | Pump Type |  | : | Vertical centrifugal, single stage
5 | Original Model |  | : | Naniwa FEV-250-2 (LR certified)
6 | Rated Flow
7 | Total Head |  | : | 21 | m
8 | Suction Head |  | : | –5 | m (below pump CL)
9 | Pump Speed |  | : | 1,750 | RPM (4-pole, 60 Hz)
10 | Hydro. Test Pressure |  | : | 0.6 | MPa (G), 30 min
11 | Motor |  | : | 37 kW, 440 V, 3Ph, 60 Hz, IP56 min.
12 | Flanges |  | : | DN250, JIS 5K
13 | Fluid |  | : | Seawater
14 | Design Life
15 | CLASS |  | : | ABS (original: LR)
IMPELLER REQUIREMENTS
1 | Material |  | : | AISI 316L Stainless Steel Cast
2 | Material Rationale |  | : | OEM grade unspecified ('SS Cast' only) — 316L explicitly required for seawater Cl⁻ resistance
3 | Dynamic Balance |  | : | ISO 1940-1 Grade G2.5 ¦ cert. required
4 | OD / Profile
5 | Trimming |  | : | Trim to rated duty point; hydraulic calc. required
6 | NDT |  | : | DP test 100% cast surfaces ¦ ABS witnessed
7 | CLASS Cert. |  | : | ABS material + product certificate
8 | Hardware
CASING WEAR RINGS
1 | Material |  | : | Synthetic Resin or PEEK
2 | Clearance |  | : | STA (per FEV-250-2 OEM tolerance)
3 | Qty |  | : | 2 per pump (casing ring + impeller ring) — 4 total
MECHANICAL SEAL
1 | Type |  | : | Single mechanical seal, external
2 | Seal Face |  | : | SiC vs SiC (seawater service)
3 | Elastomer |  | : | EPDM or FKM
4 | Pressure Rating |  | : | ≥ 0.6 | MPa (G)
5 | Temp. Rating |  | : | ≤ 60 | °C
6 | Qty |  | : | 1 set per pump — 2 sets total
VENDOR DATA — TO BE COMPLETED BY VENDOR
1 | Vendor / Manufacturer |  | : | STA
2 | Country of Manufacture |  | : | STA
3 | Part / Model No. |  | : | STA (confirm interchangeability with FEV-250-2)
4 | Actual Material |  | : | STA (with EN 10204 Type 3.1 cert.)
5 | Balance Grade Achieved
6 | Delivery Lead Time |  | : | STA | weeks ex-works
7 | Unit Weight per Set |  | : | STA | kg

## Engine-2
FPU KELIDANG
SEA WATER & CFW COOLING PUMP IMPELLER
TECHNICAL DATASHEET
| Document No: |  |  |  | Area | Date:
| Tag No.: |  |  |  | No. Req. | By:
| Operation: |  |  |  | Project | Reviewed:
| Services: |  |  |  | Job No. | Approved:
| Revision: |  |  |  | Serial No. | Page: | 5 | of | 6 | REV
CENTRAL FW COOLING PUMP — IMPELLER
PUMP SERVICE DATA (REFER NOTES)
PUMP SERVICE DATA (REFER NOTES)
1 | Service |  | : | Central Fresh Water Cooling — FPU
2 | Tag No. |  | : | CW-308X01 / 02 / 03
3 | Impeller Sets |  | : | 3 sets (2 Duty + 1 Standby)
4 | Pump Type |  | : | Vertical centrifugal, single stage
5 | Original Model |  | : | Naniwa FEV-250-2 (LR certified)
6 | Rated Flow
7 | Total Head |  | : | 25 | m
8 | Suction Head |  | : | +15 | m
9 | Pump Speed |  | : | 1,750 | RPM (4-pole, 60 Hz)
10 | Operating Temp. |  | : | 55 | °C max
11 | Hydro. Test Pressure |  | : | 0.8 | MPa (G), 30 min
12 | Motor |  | : | 37 kW, 440 V, 3Ph, 60 Hz, IP56 min.
13 | Flanges |  | : | DN250, JIS 5K
14 | Fluid |  |  | Fresh Water (cooled)
15 | Design Life
16 | CLASS |  | : | ABS (original: LR)
IMPELLER REQUIREMENTS
1 | Material |  | : | Cast Bronze — ASTM B62
2 | Composition |  | : | Cu: 87%, Sn: 6%, Zn: 6% (max) — per ASTM B62
3 | Material Rationale |  | : | Original OEM material retained — 55 °C FW service; 15-yr design life; proven in-service record
4 | Dynamic Balance |  | : | ISO 1940-1 Grade G2.5 ¦ cert. required
5 | OD / Profile |  | : | STA — identical to FEV-250-2 impeller; confirm with dimensional drawing
6 | NDT |  | : | DP test 100% cast surfaces ¦ ABS witnessed
7 | CLASS Cert. |  | : | ABS material + product certificate
8 | Hardware — Nut |  | : | Copper Alloy Rod, BS2874 (per OEM)
9 | Hardware — Key |  | : | Stainless Steel AISI 304 (per OEM)
10 | Hardware — Washers |  | : | Stainless Steel AISI 304 (per OEM)
MECHANICAL SEAL
1 | Type |  | : | Single mechanical seal, external
2 | Seal Face |  | : | Carbon vs Ceramic (FW service at 55 °C)
3 | Elastomer |  | : | EPDM
4 | Pressure Rating |  | : | ≥ 0.8 | MPa (G)
5 | Temp. Rating |  | : | ≤ 70 | °C
6 | Qty |  | : | 1 set per pump — 3 sets total
VENDOR DATA — TO BE COMPLETED BY VENDOR
1 | Vendor / Manufacturer |  | : | STA
2 | Country of Manufacture |  | : | STA
3 | Part / Model No. |  | : | STA (confirm interchangeability with FEV-250-2)
4 | Actual Material |  | : | STA (ASTM B62 cert. no.)
5 | Balance Grade Achieved |  | : | STA (ISO 1940-1 cert.)
6 | Delivery Lead Time |  | : | STA | weeks ex-works
7 | Unit Weight per Set |  | : | STA | kg

## Alternator
FPU KELIDANG
SEA WATER & CFW COOLING PUMP IMPELLER
TECHNICAL DATASHEET
| Document No: |  |  |  | Area | [8 empty] | Date:
| Tag No.: |  |  |  | No. Req. | [8 empty] | By:
| Operation: |  |  |  | Project | [8 empty] | Reviewed:
| Services: |  |  |  | Job No. | [8 empty] | Approved:
| Revision: |  |  |  | Serial No. | [8 empty] | Page: | 6 | of | 6 | REV
SEA WATER & CFW COOLING PUMP IMPELLER
INSPECTION, TEST & COMPLIANCE DECLARATION
INSPECTION AND TEST PLAN (ITP)
1 | Dimensional Inspection |  | : | 100% vs. casing drawings; interchangeability confirmed ¦ ABS witnessed
2 | Material Cert. Review |  | : | EN 10204 Type 3.1 — 100% of impellers
3 | Dynamic Balance Test |  | : | ISO 1940-1 Grade G2.5 ¦ both faces ¦ certificate required
4 | NDT — Dye Penetrant |  | : | 100% cast surfaces ¦ ASTM E165 ¦ ABS witnessed
5 | Hydro. Test — S.W. Pump |  | : | 0.6 MPa (G), 30 min ¦ ABS witnessed
6 | Hydro. Test — CFW Pump |  | : | 0.8 MPa (G), 30 min ¦ ABS witnessed
7 | Mech. Seal Pressure Test |  | : | Per manufacturer procedure ¦ leakage test included
8 | Final Visual Inspection |  | : | 100% ¦ No pitting, cracks, porosity
9 | CLASS Certificate
VENDOR DATA — TO BE COMPLETED BY VENDOR
1 | Vendor / Manufacturer |  | : | STA
2 | Country of Manufacture |  | : | STA
3 | S.W. Impeller Model / Mat. |  | : | STA (with EN 10204 Type 3.1 cert. no.)
4 | S.W. Balance Report No. |  | : | STA
5 | CFW Impeller Model / Mat. |  | : | STA (ASTM B62; with cert. no.)
6 | CFW Balance Report No. |  | : | STA
7 | Total Delivery Lead Time |  | : | STA | weeks ex-works
8 | Inspection Location |  | : | STA (City, Country)
9 | Reference Projects |  | : | STA (min. 2 similar marine pump impeller renewals)
COMPLIANCE DECLARATION — TO BE COMPLETED BY VENDOR
1 | S.W. impeller: AISI 316L SS Cast — ABS certified |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
2 | CFW impeller: Cast Bronze ASTM B62 — ABS certified |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
3 | All impellers interchangeable with FEV-250-2 casing |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
4 | ISO 1940-1 Grade G2.5 dynamic balance — all impellers |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
5 | EN 10204 Type 3.1 material certificates supplied |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
6 | DP test 100% cast surfaces — ABS witnessed |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
7 | ABS CLASS approval / certificate |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
8 | S.W. seal: SiC/SiC, EPDM/FKM, ≥0.6 MPa, ≤60°C |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
9 | CFW seal: Carbon/Ceramic, EPDM, ≥0.8 MPa, ≤70°C |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
10 | S.W. wear rings supplied (Synthetic Resin or PEEK) |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
11 | Design life 15 years — no drydocking |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
12 | Warranty ≥ 24 months from installation |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
13 | IOM Manual in English |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
14 | 2-year spare parts list submitted with bid |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
STA
STA
STA
STA
STA
STA
STA
STA
STA
STA
STA
STA
__STA___% for __STA___hour at each __STA___hour
STA
STA
STA
[6 empty] | Generator |  |  | : | STA
[6 empty] | Accessories |  |  | : | STA
STA
STA
STA
complete datasheet to be provided by manufacturer for review
to be provided by manufacturer for review
STA
STA
[6 empty] | Type | : | STA |  |  | Quantity | : | STA
[6 empty] | Type | : | STA |  |  | Quantity | : | STA
[6 empty] | Type | : | STA |  |  | Quantity | : | STA
STA
STA
STA