## MISC-Cover Page
[8 empty] | OWNER Document No: |  | KLD-NVOE-MSE-TDS-3072SP-30001- |  |  | REV | A0
[8 empty] | COMPANY Document No: |  | KCD-FPU-EXE-NVOE-99-MRN-TDS-0006- |  |  | REV | A
LOCAL WATER MIST EXTINGUISHING SYSTEM TECHNICAL DATASHEET | [11 empty] | Page No: 1 of 6
| PROJECT TITLE |  |  | : | PROVISION OF LEASE, OPERATE AND MAINTAIN (O&M) OF FLOATING PRODUCTION UNIT (FPU) FOR KELIDANG CLUSTER DEVELOPMENT PROJECT
| COMPANY |  |  | : | PETRONAS CARIGALI BRUNEI LTD
| CONTRACT NO |  |  | : | PCBL/2023/PROJECT/003
| DOCUMENT TITLE |  |  | : | LOCAL WATER MIST EXTINGUISHING SYSTEM TECHNICAL DATASHEET
| DOCUMENT REVIEW CLASSIFICATION |  |  | : | X
| SECURITY CLASSIFICATION |  |  | : | OPEN
| SUBCONTRACTOR DOC NO |  |  | : | XXX-XXX-XXXXXX-XXXX
B0 |  | 08.05.2026 | Inter-Disciplinary Check |  |  | HSN | HHK |  | HHK
REV |  | DATE | DESCRIPTION |  |  | PREPARED | REVIEW |  | APPROVED | REVIEWED | VERIFIED |  | ACKN'D
[6 empty] | CONTRACTOR |  |  |  | COMPANY

## Revision History
|  |  |  | OWNER Document No: | KLD-NVOE-MSE-TDS-3072SP-30001- |  | REV
|  |  |  | COMPANY Document No: | KCD-FPU-EXE-NVOE-99-MRN-TDS-0006 |  | REV | A
LOCAL WATER MIST EXTINGUISHING SYSTEM TECHNICAL DATASHEET | [5 empty] | Page No: 2 of 6
RECORD OF CHANGES
REVISION | DATE |  | DESCRIPTION
A0 | 2026-05-08 |  | Issued for Inter-DIsciplinary Check
HOLD LISTS
REVISION |  | DESCRIPTION
Note on A1: [스레드 댓글] 사용 중인 버전의 Excel에서 이 스레드 댓글을 읽을 수 있지만 파일을 이후 버전의 Excel에서 열면 편집 내용이 모두 제거됩니다. 자세한 정보: https://go.microsoft.com/fwlink/?linkid=870924. 댓글: Area Specific. Responsible engineer to change is Area Code 10 (FPU) / 20 (Topside) / 30 (Hull & Marine) / 40 (Mooring) / 50 (Subsea). To be deleted which not applicable

## Notes and holds
FPU KELIDANG
LOCAL WATER MIST EXTINGUISHING SYSTEM
TECHNICAL DATASHEET
| Document No: |  | KLD-NVOE-MSE-TDS-3072SP-30001 |  | Area | HULL & MARINE | Date: | 2026-05-08
| Tag No.: |  | SP-308401/402/403 |  | No. Req. | 1 | Prepared : | HSN
| Operation: |  | FIRE SUPPRESSION — MACHINERY SPACES |  | Project | FPU KELIDANG | Reviewed: | HHK
| Services: |  | LOCAL WATER MIST EXTINGUISHING SYSTEM |  | Job No. | N/A | Approved: | HHK
| Revision: |  | A0 |  | Serial No. | N/A | Page: | 3 | of | 6 | REV
LOCAL WATER MIST EXTINGUISHING SYSTEM
NOTES AND HOLDS
1 |  | STA = Supplier to advise ¦ STC = Supplier to confirm ¦ TBA = To be advised
2 |  | Supplier shall complete all items in this datasheet and return with technical bid.
3 |  | Design life: 25 years minimum. No drydocking required (UWILD notation).
4 |  | Environment: tropical offshore, ambient 20–38 °C, RH up to 100 %, saline marine atmosphere.
5 |  | Surface preparation and coating per project requirements; suitable for exposed marine environment.
6 |  | System shall be a complete functional package: pumps, piping, valves, nozzles, control panel, instrumentation.
7 |  | Extinguishing medium: distilled / demineralised fresh water only. TDS < 500 ppm, pH 6.5–8.5.
8 |  | Mandatory compliance: IMO MSC/Circ.1167 (primary), NFPA 750 (supplementary), ABS CLASS approval.
9 |  | Nozzles: open (non-automatic) deluge type. K-factor, spray pattern test report and fire-test certificate with bid.
10 |  | Pre-discharge alarm: audible + visual, per zone entry; minimum 30 sec before nozzle discharge.
11 |  | Pumps: 3 units (Duty / Standby / Reserve). Auto-start on pressure drop; sequential start sequence.
12 |  | Control panel: IP56, 24 VDC UPS-backed, battery autonomy ≥ 30 min. FAT + SAT required.
13 |  | FAT witnesses: COMPANY representative + ABS CLASS Surveyor; 2 weeks advance notice.
14 |  | Material certs: EN 10204 Type 3.1 for all pressure-retaining parts.
15 |  | GA drawing with centre of gravity for pump skid to be provided with bid.

## Engine-1
FPU KELIDANG
LOCAL WATER MIST EXTINGUISHING SYSTEM
TECHNICAL DATASHEET
| Document No: |  |  |  | Area | Date:
| Tag No.: |  |  |  | No. Req. | By:
| Operation: |  |  |  | Project | Reviewed:
| Services: |  |  |  | Job No. | Approved:
| Revision: |  |  |  | Serial No. | Page: | 4 | of | 6 | REV
LOCAL WATER MIST EXTINGUISHING SYSTEM
GENERAL INFORMATION (REFER NOTES)
GENERAL INFORMATION (REFER NOTES)
1 | Application |  | : | Local Water Mist Extinguishing System (LWMS) — FPU Machinery Spaces
2 | Quantity |  | : | 1 system (3 pump units: 1 × Duty, 1 × Standby, 1 × Reserve)
3 | Location (pumps) |  | : | AFT Machinery Room (Pump No.1 & 2) ¦ FWD Machinery Room (Pump No.3)
4 | System Type |  | : | Fixed local application, open-nozzle deluge, low-to-medium pressure water mist
5 | Package Size |  | : | STA
SYSTEM DESIGN CONDITIONS
1 | Operating Principle |  | : | Open-nozzle deluge — all nozzles per zone discharge simultaneously on activation
2 | Pressure Classification |  | : | Low-to-medium pressure water mist (per NFPA 750)
3 | Protected Zones |  | : | 7 zones — 1 independent deluge valve per zone
4 | Max. Simultaneous Zones |  | : | 1 zone at a time
5 | Design Flow Rate per Pump |  | : | 10.99 | m³/h min.
6 | System Pressure (outlet) |  | : | 1.02 | MPa (G)
7 | Hydrostatic Test Pressure
8 | Water Source |  | : | Fresh Water Tank — Port [F.W.TK(P)], DN40 inlet
9 | Water Quality |  | : | Distilled / Demineralised ¦ TDS < 500 ppm ¦ pH 6.5–8.5
10 | Blowing Medium |  | : | G/S Air — DN25 at header (post-discharge pipe purging)
11 | Ambient Temperature |  | : | 0 to +55 | °C
12 | Relative Humidity |  | : | Up to 100 | %
13 | Activation |  | : | Auto (FGS signal) + Manual release ¦ Pre-alarm ≥ 30 sec
14 | Electrical Supply
15 | Control Voltage |  | : | 24 VDC, UPS-backed
PROTECTED AREAS (7 ZONES)
1 | Zone 1 — No.1 Generator Engine (incl. Turbocharger)
2 | Zone 2 — No.2 Generator Engine (incl. Turbocharger) |  | : | Engine Room / Pump Room — Auto + Manual
3 | Zone 3 — No.3 Generator Engine (incl. Turbocharger) |  | : | Engine Room / Pump Room — Auto + Manual
4 | Zone 4 — Auxiliary Boiler No.1 |  | : | Boiler Room / Machinery Room — Auto + Manual
5 | Zone 5 — Auxiliary Boiler No.2 |  | : | Boiler Room / Machinery Room — Auto + Manual
6 | Zone 6 — Aft Machinery Room |  | : | Aft Machinery Room — Auto + Manual
7 | Zone 7 — Main Machinery Room

## Engine-2
FPU KELIDANG
LOCAL WATER MIST EXTINGUISHING SYSTEM
TECHNICAL DATASHEET
| Document No: |  |  |  | Area | Date:
| Tag No.: |  |  |  | No. Req. | By:
| Operation: |  |  |  | Project | Reviewed:
| Services: |  |  |  | Job No. | Approved:
| Revision: |  |  |  | Serial No. | Page: | 5 | of | 6 | REV
LOCAL WATER MIST EXTINGUISHING SYSTEM
PUMP, NOZZLE & PIPING SPECIFICATIONS
PUMP UNIT SPECIFICATIONS
1 | Number of Pumps |  | : | 3 units (1 × Duty, 1 × Standby, 1 × Reserve)
2 | Pump Type |  | : | Multistage centrifugal or plunger/piston
3 | Rated Flow (each pump) |  | : | 10.99 | m³/h min. (≈183 L/min)
4 | Rated Discharge Pressure |  | : | 1.02 | MPa (G) (≈10.2 bar.G)
5 | Casing Material |  | : | Stainless Steel 316L minimum
6 | Seal Type
7 | Motor Voltage |  | : | 440 V, 3-phase, 60 Hz
8 | Motor IP Rating |  | : | IP56 minimum (Marine duty, Class F insulation)
9 | Motor Start Method |  | : | Star-delta or VFD (soft-start preferred; STC)
10 | Motor Certification |  | : | IECEx / ATEX or equivalent (per area classification)
11 | Suction Strainer |  | : | Y- or basket-type, 316L SS, mesh ≤ 0.8 mm; ΔP indicator
12 | Pressure Relief Valve |  | : | 1.12 MPa (G) (≈110 % rated) — 316L SS body
13 | Check Valve (discharge) |  | : | Swing or piston, SS316L, 1 per pump
14 | Pressure Gauge — Suction |  |  | 0–0.6 MPa, local, SS Bourdon tube
15 | Pressure Gauge — Discharge
16 | Pressure Transmitter |  | : | 2 pcs on main header; 4–20 mA; auto-start & remote monitoring
17 | Skid Frame |  | : | Hot-dip galvanised steel or SS304/316; drip tray included
18 | Auto-start Logic |  | : | Pressure drop → Duty → Standby → Reserve (set points STC)
NOZZLE SYSTEM SPECIFICATIONS
1 | Nozzle Type |  | : | Open (non-automatic), flat-fan or full-cone deluge
2 | Standard |  | : | NFPA 750 ¦ Dv0.99 < 1000 µm ¦ IMO MSC/Circ.1167
3 | K-factor |  | : | STA (per vendor hydraulic calc.; provided with bid)
4 | Min. Pressure at Nozzle |  | : | STA (at furthest nozzle; per vendor calc.)
5 | Body Material |  | : | AISI 316L stainless steel
6 | Orifice Material |  | : | SS or ceramic corrosion-resistant insert
7 | Connection |  | : | NPT or BSP threaded; SS316L fittings
8 | Inline Strainer |  | : | Mesh ≤ 0.8 mm, 316L SS, upstream of each nozzle
9 | Spray Coverage |  | : | All fire-risk surfaces per IMO MSC/Circ.1167
10 | Quantity per Zone |  | : | STA (per CLASS-approved hydraulic calculation)
11 | Fire Test Certificate |  | : | CLASS-accepted; IMO MSC/Circ.1167; ABS approval required
PIPING AND VALVE SPECIFICATIONS
1 | Pipe Material |  | : | ASTM A312 TP316L seamless SS; ASME B31.1
2 | Pipe Sizes |  | : | DN15 / DN25 / DN40 / DN50 (per P&ID)
3 | Pipe Rating |  | : | ASME Class 150 min., Sch 40S or heavier
4 | Flanges |  | : | ASME B16.5 Class 150, SS316L, raised face
5 | Deluge Valve |  | : | Electrically actuated, spring-return, fail-closed; SS316L; 1 per zone
6 | Isolation Valves |  | : | Full-bore ball valves, SS316L, lockable
7 | Check Valves |  | : | Swing or piston, SS316L, 1 per pump discharge
8 | Test / Drain Valves |  | : | Manual ball valves at each zone low point, DN25 min.
9 | Air Blowing Connection |  | : | DN25 flanged at main header; G/S Air with check valve
10 | Gaskets |  | : | PTFE or EPDM; no asbestos; rated to 120 °C
11 | Fasteners |  | : | A4-70 SS316 (wetted) ¦ A2-70 (structural)

## Alternator
FPU KELIDANG
LOCAL WATER MIST EXTINGUISHING SYSTEM
TECHNICAL DATASHEET
| Document No: |  |  |  | Area | [8 empty] | Date:
| Tag No.: |  |  |  | No. Req. | [8 empty] | By:
| Operation: |  |  |  | Project | [8 empty] | Reviewed:
| Services: |  |  |  | Job No. | [8 empty] | Approved:
| Revision: |  |  |  | Serial No. | [8 empty] | Page: | 6 | of | 6 | REV
LOCAL WATER MIST EXTINGUISHING SYSTEM
CONTROL SYSTEM ¦ INSPECTION & TEST ¦ VENDOR DATA
CONTROL SYSTEM SPECIFICATIONS
1 | Control Panel |  | : | System Main Control Panel + Local Pump Control Panel (vendor scope)
2 | Control Voltage |  | : | 24 VDC, UPS-backed; battery autonomy ≥ 30 min
3 | Panel IP Rating |  | : | IP56 minimum
4 | Panel Material |  | : | SS316L or powder-coated mild steel
5 | Zone Indication |  | : | Lamp + LED per zone: Fault / Armed / Discharge
6 | Manual Release |  | : | Break-glass or key-switch at each zone entry
7 | FGS Interface |  | : | Dry contact input from FPU Fire & Gas System
8 | Pre-discharge Alarm |  | : | Audible horn + visual strobe; ≥ 30 sec before discharge
9 | Pump Auto-start
10 | Area Classification |  | : | ATEX/IECEx Zone 1 or 2 (confirm per area drawings)
11 | Cabling |  | : | Fire-resistant cable within package battery limits
12 | Remote Alarm Output |  | : | Dry contacts to FPU AMS: Fault / Zone Discharge / Pump Run
INSPECTION, TESTING & QUALITY REQUIREMENTS
1 | Hydrostatic Test |  | : | 1.53 MPa (G), ≥ 30 min ¦ Witness: COMPANY + CLASS
2 | Pump Performance (FAT) |  | : | ISO 9906 Grade 1 ¦ Flow ≥ 10.99 m³/h @ 1.02 MPa ¦ H-Q curves required
3 | Nozzle Fire Test |  | : | IMO MSC/Circ.1167 ¦ Valid CLASS fire-test certificate required
4 | Control Panel FAT |  | : | Full simulation: alarm, auto-start, manual release, remote signals
5 | FAT Witnesses |  | : | COMPANY + ABS CLASS Surveyor ¦ 2 weeks advance notice
6 | Material Certificates |  | : | EN 10204 Type 3.1 for all pressure-retaining parts
7 | SAT (on site) |  | : | Discharge test each zone; pump start/run; spray pattern confirmation
VENDOR DATA — TO BE COMPLETED BY VENDOR
1 | Vendor / Manufacturer |  | : | STA
2 | Country of Manufacture |  | : | STA
3 | System / Package Model |  | : | STA
4 | Pump Make & Model |  | : | STA (pump curve with bid)
5 | Motor Make & Model |  | : | STA (motor datasheet with bid)
6 | Nozzle Make & K-factor |  | : | STA (spray test report with bid)
7 | CLASS Fire Test Cert. No. |  | : | STA (ABS or equivalent; attach copy)
8 | Skid Dimensions (L×W×H) |  | : | STA | mm
9 | Skid Dry Weight |  | : | STA | kg
10 | Operating Weight |  | : | STA | kg
11 | Delivery Lead Time |  | : | STA | weeks (ex-works)
12 | FAT Location |  | : | STA (City, Country)
13 | Reference Projects |  | : | STA (min. 2 offshore / marine LWMS projects)
COMPLIANCE DECLARATION — TO BE COMPLETED BY VENDOR
1 | System: open-nozzle deluge water mist |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
2 | Pump flow ≥ 10.99 m³/h per pump |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
3 | Pump pressure 1.02 MPa (G) |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
4 | 3 pumps: Duty / Standby / Reserve |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
5 | ABS CLASS fire-test certificate (nozzle) |  | : | ☐ YES / ☐ NO / ☐ DEVIATE
6 | ABS CLASS arrangement approval
7 | 316L SS — distilled water compatible |  | : | ☐ YES / ☐ NO / ☐ DEVIATE |  | STA
8 | IMO MSC/Circ.1167 compliance |  | : | ☐ YES / ☐ NO / ☐ DEVIATE |  | STA
9 | NFPA 750 compliance (supplementary) |  | : | ☐ YES / ☐ NO / ☐ DEVIATE |  | STA
10 | Design life 25 years |  | : | ☐ YES / ☐ NO / ☐ DEVIATE |  | STA
11 | Motor IP56 minimum |  | : | ☐ YES / ☐ NO / ☐ DEVIATE |  | STA
12 | 24 VDC UPS-backed control panel |  | : | ☐ YES / ☐ NO / ☐ DEVIATE |  | STA
13 | Pre-discharge alarm ≥ 30 sec |  | : | ☐ YES / ☐ NO / ☐ DEVIATE |  | STA
14 | FAT witnessed by COMPANY + CLASS |  | : | ☐ YES / ☐ NO / ☐ DEVIATE |  | STA
15 | IOM Manual in English |  | : | ☐ YES / ☐ NO / ☐ DEVIATE |  | STA
16 | 2-year + critical spare parts list with bid |  | : | ☐ YES / ☐ NO / ☐ DEVIATE |  | STA
STA
STA
__STA___% for __STA___hour at each __STA___hour
STA
STA
STA
[6 empty] | Generator |  |  | : | STA
[6 empty] | Accessories |  |  | : | STA
STA
STA
STA
complete datasheet to be provided by manufacturer for review
to be provided by manufacturer for review
STA
STA
[6 empty] | Type | : | STA |  |  | Quantity | : | STA
[6 empty] | Type | : | STA |  |  | Quantity | : | STA
[6 empty] | Type | : | STA |  |  | Quantity | : | STA
STA
STA
STA