| PROJECT | FPU KELIDANG — PETRONAS CARIGALI BRUNEI LTD | DOC NO. | KLD-NVOE-MSE-TRP-3050SW-30001-A0 |
| --- | --- | --- | --- |
| TITLE | TECHNICAL REQUISITION PACKAGE — SEA WATER COOLING PUMP & CENTRAL FW COOLING PUMP IMPELLER RENEWAL |  | REV: A0 |
| CONTRACT | PCBL/2023/PROJECT/003 | DATE | 08 May 2026 |

# 1.  INTRODUCTION

## 1.1  Purpose

This Technical Requisition Package (TRP) is issued by PETRONAS Carigali Brunei Ltd (PCBL) for procurement of replacement impellers, casing wear rings, and mechanical seals for the Sea Water (S.W.) Cooling Pumps and Central Fresh Water (CFW) Cooling Pumps on FPU Kelidang. The FPU has a 15-year design life with no scheduled drydocking (UWILD notation).

## 1.2  Document References

| Doc No. | Title | Rev. |
| --- | --- | --- |
| KLD-NVOE-MSE-SOW-3050SW-30001 | Scope of Work — S.W. & CFW Pump Impeller Renewal | A0 |
| KLD-NVOE-MSE-SPN-3050SW-30001 | Equipment Specification — Pump Impeller | A0 |
| KLD-NVOE-MSE-TDS-3050SW-30001 | Technical Datasheet — Pump Impeller | A0 |
| KLD-NVOE-TSA-PID-3050SW-30001-001 | P&ID — Seawater Service System | B0 |

# 2.  PROJECT AND EQUIPMENT SUMMARY

| Parameter | Value |
| --- | --- |
| Project | Kelidang Cluster Development Project — FPU Conversion |
| COMPANY | PETRONAS Carigali Brunei Ltd (PCBL) |
| Contract No. | PCBL/2023/PROJECT/003 |
| FPU Type | Ship-type FPU, single hull, permanently moored |
| Classification Society | American Bureau of Shipping (ABS) |
| Original CLASS | Lloyd's Register (LR) |
| Design Life | 15 years — No drydocking (UWILD notation) |
| Location | Offshore Brunei Darussalam — Tropical marine environment |
| Ambient Temp. | 20–38 °C, RH up to 100 % |
| Revision / Date | A0 / 08 May 2026 |
| Prepared By | HSN ¦ Checked: HHK ¦ Approved: HHK |

# 3.  ITEMS TO BE PURCHASED

Vendor shall supply a complete set of replacement impellers, casing wear rings, and mechanical seals for the following pumps:

| Item | Tag No. | Description | Qty | Original Model | Material |
| --- | --- | --- | --- | --- | --- |
| 1 | SW-308X01/02 | S.W. Cooling Pump Impeller | 2 sets | Naniwa FEV-250-2 | AISI 316L SS Cast |
| 2 | SW-308X01/02 | S.W. Pump Casing Wear Rings (pair) | 2 sets | FEV-250-2 | Synthetic Resin / PEEK |
| 3 | SW-308X01/02 | S.W. Pump Mechanical Seal | 2 sets | FEV-250-2 | SiC/SiC, EPDM/FKM |
| 4 | CW-308X01~03 | Central CFW Pump Impeller | 3 sets | Naniwa FEV-250-2 | Cast Bronze ASTM B62 |
| 5 | CW-308X01~03 | CFW Pump Mechanical Seal | 3 sets | FEV-250-2 | Carbon/Ceramic, EPDM |
| 6 | All above | Associated Hardware per impeller set | 5 sets | — | SS316L / SS304 / Cu Alloy per OEM |

# 4.  TECHNICAL REQUIREMENTS SUMMARY

## 4.1  Sea Water Cooling Pump (FEV-250-2)

| Parameter | Value | Remark |
| --- | --- | --- |
| Flow Rate | 420 m³/h min. |  |
| Total Head | 21 m |  |
| Pump Speed | 1,750 RPM | 4-pole, 60 Hz |
| Fluid | Seawater |  |
| Hydro. Test Pressure | 0.6 MPa (G) | 30 min |
| Motor | 37 kW, 440V, IP56 | 3Ph, 60Hz |
| Flange | DN250, JIS 5K |  |
| Impeller Material | AISI 316L SS Cast | OEM grade unspecified — 316L explicitly required |
| Seal Face | SiC vs SiC | Seawater service |
| Design Life | 15 years, no drydocking | UWILD notation |

## 4.2  Central FW Cooling Pump (FEV-250-2)

| Parameter | Value | Remark |
| --- | --- | --- |
| Flow Rate | 360 m³/h min. |  |
| Total Head | 25 m |  |
| Operating Temp. | 55 °C max | FW service |
| Hydro. Test Pressure | 0.8 MPa (G) | 30 min |
| Motor | 37 kW, 440V, IP56 | 3Ph, 60Hz |
| Flange | DN250, JIS 5K |  |
| Impeller Material | Cast Bronze ASTM B62 | Original OEM material — no upgrade required for 55°C / 15yr |
| Seal Face | Carbon vs Ceramic | FW 55°C service |
| Design Life | 15 years, no drydocking | UWILD notation |

# 5.  QUALITY REQUIREMENTS AND INSPECTION PLAN

| Test / Inspection | Requirement | Witness |
| --- | --- | --- |
| Dimensional Inspection | 100% vs. FEV-250-2 casing drawings; full interchangeability | ABS + COMPANY |
| Material Cert. Review | EN 10204 Type 3.1 for all impellers | COMPANY |
| Dynamic Balance Test | ISO 1940-1 Grade G2.5; both faces; certificate required | ABS + COMPANY |
| NDT — Dye Penetrant | 100% cast surfaces; ASTM E165 | ABS + COMPANY |
| Hydrostatic Test — S.W. | 0.6 MPa (G), 30 min | ABS + COMPANY |
| Hydrostatic Test — CFW | 0.8 MPa (G), 30 min | ABS + COMPANY |
| Mech. Seal Pressure Test | Per manufacturer procedure; leakage test | COMPANY |
| Final Visual Inspection | 100%; no pitting, cracks, or surface defects | ABS + COMPANY |
| CLASS Certification | ABS material + product certificate; issued before dispatch | ABS |

# 6.  VENDOR DOCUMENTATION REQUIREMENTS

| No. | Document | Stage | Copies |
| --- | --- | --- | --- |
| 1 | Dimensional drawing — interchangeability with FEV-250-2 | With Bid | 2 hard + PDF |
| 2 | Material proposal (grade, ASTM/EN standard) | With Bid | PDF |
| 3 | Balance grade capability (ISO 1940-1) | With Bid | PDF |
| 4 | Reference project list (min. 2 similar) | With Bid | PDF |
| 5 | Preliminary ITP / QCP | With Bid | PDF |
| 6 | EN 10204 Type 3.1 Material Test Certs | Before Dispatch | 2 hard + PDF |
| 7 | Dynamic Balance Test Report | Before Dispatch | 2 hard + PDF |
| 8 | Dye Penetrant Test Report | Before Dispatch | 2 hard + PDF |
| 9 | Hydrostatic Test Certificate | Before Dispatch | 2 hard + PDF |
| 10 | ABS CLASS Certificate | Before Dispatch | 2 hard + PDF |
| 11 | Mechanical Seal Pressure Test Report | Before Dispatch | PDF |
| 12 | Installation and Maintenance Manual (IOM) | With Delivery | 2 hard + PDF |
| 13 | 2-Year Spare Parts List | With Bid | PDF |
| 14 | Packing List | With Delivery | 2 hard + PDF |

# 7.  DELIVERY AND COMMERCIAL REQUIREMENTS

| Item | Requirement |
| --- | --- |
| Delivery Terms | CIF Brunei Darussalam / DAP FPU Site (INCOTERMS 2020) |
| Packaging | Export-grade; corrosion-inhibited; suitable for sea freight |
| Marking | Part number, material grade, heat number, PO number on each item |
| Bid Validity | Minimum 90 days from bid submission |
| Warranty | Minimum 24 months from date of installation or 30 months from delivery (whichever is earlier) |
| Spare Parts | 2-year operational spares list required with bid |
| Lead Time | Vendor to advise (STA) from Purchase Order to ex-works |

# 8.  VENDOR QUALIFICATION REQUIREMENTS

Minimum 5 years experience in supply of centrifugal pump impellers for marine / offshore applications.

Experience with Naniwa FEV-series or equivalent vertical centrifugal pump impeller replacement preferred.

ISO 9001:2015 certification or equivalent.

Ability to obtain ABS CLASS certification for supplied items.

Minimum 2 reference projects supplying impellers for marine / offshore cooling pumps.

In-house or accredited facility capability for dynamic balancing to ISO 1940-1 Grade G2.5.

# 9.  BIDDER INSTRUCTIONS

Bidders shall submit the following with their technical and commercial bid:

Completed Technical Datasheet (KLD-NVOE-MSE-TDS-3050SW-30001) — all STA/STC items filled in.

Dimensional drawings confirming interchangeability with FEV-250-2 casing.

Compliance Declaration (from TDS) — deviations clearly noted.

Company profile and reference project list.

Preliminary ITP.

2-year spare parts list with indicative pricing.

Firm delivery lead time from PO to ex-works.

# 10.  GENERAL NOTES

All correspondence shall be in English.

COMPANY reserves the right to visit the Vendor's manufacturing facility at any time during order execution.

Non-conformance reports (NCRs) to be submitted to COMPANY within 24 hours of identification.

COMPANY and ABS Surveyor shall have free access for inspection at all times during manufacture.

No sub-contracting of primary impeller manufacture without prior written COMPANY approval.